## Inputs
Guidance - read the guidelines document to understand how this sheet fits in with the feasibilty calculator for heat reuse projects during the early stages
For calculation purposes, each decision-tree choice is treated as an explicit assumption and must be documented with associated data inputs within the Decision & Assumptions Excel. The calculator will only use values captured through this structure.
Scenario 1-1 : Temperature increase at the perimeter of the data center without a fixed heat price (=> heat price)
The data center upgrades waste heat to match the district heating network temperature requirements. This involves additional energy consumption and integration of heat pump systems. No predefined heat price is assumed in this scenario. The objective is to determine the break-even heat selling price at the data center boundary. This price ensures cost recovery and project viability. Heat pump electricity consumption is included, leading to an increase in the data center PUE.
Scenario 1-2 : Temperature increase at the data center perimeter with a fixed heat price (=> P&L)
The data center similarly increases heat temperature to meet network specifications. In this case, the heat selling price is imposed by the district heating operator. The focus is on evaluating the project’s financial performance. A full profit and loss (P&L) analysis is conducted. This determines profitability under fixed market conditions. Heat pump electricity consumption is included, leading to an increase in the data center PUE.
Scenario 2 : No temperature increase (=> heat price)
The data center exports waste heat without any temperature upgrade. This limits compatibility with district heating network requirements. No fixed heat price is assumed in this configuration. The objective is to determine the achievable heat selling price. This reflects the lower-grade heat and its market value. Reduced chiller electricity consumption improves efficiency, leading to a decrease in the data center PUE.
SECTION A — PROJECT & BASELINE FEASIBILITY
A1 | Q1. Project name & reference date
→ activates:
| Project Name | PAR18
| Date | 2025-10-31
A2 | Q2. Is there a confirmed heat off-taker? | Yes
No → STOP (calculator disabled)
A3 | Q3. What are the conditions for heat transfer?
| Scenario 1-1 : Do you need to supply heat at the same temperature as the heat off-taker? | Yes
“I, data centre operator, am going to operate the heatpump even though I have heard my PUE will be impacted because we decided as a business that this is the best way to more forward” [This means heat pump included in CAPEX and OPEX calculations and the PUE impact tab shows how that will impact PUE.
| Scenario 1-2 : Do you know the target heat price of the heat off taker? (€/MWh) | Yes
if not specified : Scnearion 1-1 Results - heat price at the data center outlet
| → activates (if yes): Scenario 1-2 Results : P&L of the projects | amount? | 95
| Scenario 2 : The heat is delivered at the data center's outlet temperature, regardless of the intended use | No
I am (data centre operator) for sure NOT going to buy or operate a heatpump for this heat reuse project. It is completely outside of my scope and the job of the district heat network. If they get a connection on my site, it will be submetered directly to them for payments.” [This means the heat pump is excluded from OPEX and CAPEX calculations and there is no PUE impact.
A4 | Q4. Impacts on PUE - Electrical Consumption
| What is the Total Facility Energy Consumption for last 12 months? (MWh) | 175200
| What is the IT Equipment Energy Consumtion? (MWh) | 133880
| SCENARIO 1-1 & 1-2 |  |  |  |  | SCENARIO 2
SECTION B — HEAT AVAILABILITY & OPERATING PROFILE |  |  |  |  | SECTION B — HEAT AVAILABILITY & OPERATING PROFILE
B1 | Q1. What is the Annual available energy needed (MWh) | 6000 |  |  | B1 | Q1. What is the Annual available energy needed (MWh) | 6000
B2 | Q2. Do you know how many hours per year is this heat available? | No |  |  | B2 | Q2. Do you know how many hours per year is this heat available? | No
| if not specified, the usage time will be considered over the heat season period (Nov --> March) |  |  |  |  | if not specified, the usage time will be considered over the heat season period (Nov --> March)
| → activates (if yes): | simulated | own data |  |  | → activates (if yes): | simulated | own data
| Usage rate (hours/year) | 3624 |  |  |  | Usage rate (hours/year) | 3624
B3 | Q3. Do you know the heating power required by the district heating system? | No |  |  | B3 | Q3. Do you know the heating power required by the district heating system? | No
| if not specified, the energy volume (in MWh) will be smoothed over the period |  |  |  |  | if not specified, the energy volume (in MWh) will be smoothed over the period
| → activates (if Yes): | simulated | own data |  |  | → activates (if Yes): | simulated | own data
| Heat power demand (kW) | 1655.6291 |  |  |  | Heat power demand (kW) | 1655.6291
SECTION C — TEMPERATURE LEVELS & HEAT PUMP NEED |  |  |  |  | SECTION C — TEMPERATURE LEVELS & HEAT PUMP NEED
C1 | Q6. What are the DC water loop temperatures? |  |  |  | C1 | Q6. What are the DC water loop temperatures?
| → activates: |  |  |  |  | → activates:
| DC inlet water temperature (°C) | 19 |  |  |  | DC inlet water temperature (°C) | 19
| DC outlet water temperature (°C) | 29 |  |  |  | DC outlet water temperature (°C) | 29
C2 | Q7. What supply temperature is required by the heat network? |  |  |  | C3 | Q8. Is a heat pump required to reach this temperature? | Yes
| → activates: |  |  |  |  | No (direct heat reuse)
| Desired outlet temperature (°C) | 85 |  |  |  | → activates (if Yes):
C3 | Q8. Is a heat pump required to reach this temperature? | Yes |  |  | SECTION D — DISTANCE
No (direct heat reuse)
C4 | Q9. Medium COP heat pump ? | 3.18 |  |  | D1 | Q10. Distance from DC to heat network connection point?
→ activates:
| This is a critical decision gate. |  |  |  |  | Distance from connection to heating network (m) - only used for heat losses in Data Center perimeter | 100
If “Yes”, electricity cost becomes structurally relevant later.
SECTION E — CAPEX RESPONSIBILITY & COST BLOCKS
SECTION D — DISTANCE
[5 empty] | E1 | Q12. Do you want to use simulated CAPEX data for equipment?
D1 | Q10. Distance from DC to heat network connection point? |  |  |  |  | → if Yes, activates corresponding inputs: |  | simulated | own data
| → activates: |  |  |  |  | Exchanger cost | Yes | 79470.1987
| Distance from connection to heating network (m) - only used for heat losses in Data Center perimeter | 100 |  |  |  | Cost of pump & fixed equipment | Yes | 248344.3709
[6 empty] | Study cost | Yes | 87665.5629
SECTION F — CAPEX RESPONSIBILITY & COST BLOCKS | [5 empty] | Control/Automation | Yes | 184097.6821
[5 empty] | E2 | Q13. Should contingency / unknown risk be included? | Yes
F1 | Q12. Do you want to use simulated CAPEX data for equipment? |  |  |  |  | → activates if yes
| → if Yes, activates corresponding inputs: |  | simulated | own data |  | Unknown risk (%) | 10%
| Exchanger cost | Yes | 79470.1987
| Heat Pump cost | Yes | 1276490.0662 |  | E3 | Q14. Are subsidies included in the economic case? | No
| Cost of pump & fixed equipment | Yes | 248344.3709 |  |  | → activates if yes |  | indicated
| Electrical connection cost | Yes | 149006.6225 |  |  | Subsidy (EUR) | 0
| Study cost | Yes | 87665.5629
| Control/Automation | Yes | 184097.6821 |  | SECTION F — ELECTRICITY COST (ONLY IF TRIGGERED)
F2 | Q13. Should contingency / unknown risk be included? | Yes |  |  | F1 | Q19. What is the electricity for heat recovery equipment? (pumps)
| → activates if yes |  |  |  |  | → activates :
| Unknown risk (%) | 20% |  |  |  | Cost of electricity (EUR/kWh) | 0.14
[6 empty] | Electricty inflation over next 20 years (%) | 2
F3 | Q14. Are subsidies included in the economic case? | Yes
| → activates if yes |  | indicated |  |  | This question should be greyed out unless a heat pump is selected.
| Subsidy (EUR) | Amount? | 588000
SECTION G — FINANCIAL & OPERATING ASSUMPTIONS
G1 | Q15. Economic lifetime / contract duration (years)?
→ activates:
| Amortization period (years) | 20
G2 | Q16. Discount rate to be applied?
→ activates:
| Discount rate (%) | 6
G3 | Q17. Annual O&M as % of CAPEX?
→ activates:
| Annual O&M (% of CAPEX) | 5
G4 | Q18. Heat Indexation?
→ activates:
| Indexation of heating prices over next 20 years (%) | 2
SECTION H — ELECTRICITY COST (ONLY IF TRIGGERED)
H1 | Q19. Who pays for electricity for heat recovery equipment? (Heatpump)
| DC operator | Yes
| Heat network | No
| Not applicable (no heat pump) | No
→ activates (if DC operator):
| Cost of electricity (EUR/kWh) | 0.14
| Electricty inflation over next 20 years (%) | 2
This question should be greyed out unless a heat pump is selected.
Note on J64: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: I think we should add in a question to indicate if the DC needs to plan for covering that (in scope or out of scope assumption)
Note on C72: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: I think we should add in a question to indicate if the DC needs to plan for covering that (in scope or out of scope assumption)

## Results-P&L
SCENARIO 1-1 RESULTS : Calculation of the price of heat at the data center outlet
CAPEX | 2430089.404 | EUR
Subsidies | 588000 | EUR
Total CAPEX | 1842089.404 | EUR
Annualised CAPEX (EUR/year) | 160601.7486 | EUR/year
Annual O&M - excluding electricity | 72902.6821 | EUR/year
Electricty Cost | 285952.1944 | EUR/year
Total Energy saved (EUR/year) | 25095.1516 | EUR/year
Contract duration | 20 | years
PUE (adjusted) | 1.3226 |  | PUE value after heat reuse, integrating electricity consumption by heat pumps operated by data center operator
Total annual cost | 494361.4735 | EUR/year
Annual energy delivered | 5558.07 | MWh/year
DC Heat Price | 88.9448 | EUR/MWh
SCNEARIO 1-2 RESULTS : P&L in the case where the price of heat is given by the heat off taker
Target Heat Price (EUR/MWh) | 95
Target Heat Price / Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 15 | 16 | 17 | 18 | 19 | 20
CAPEX |  | 160601.7486 | 160601.7486 | 160601.7486 | 160601.7486 | 160601.7486 | 160601.7486 | 160601.7486 | 160601.7486 | 160601.7486 | 160601.7486 | 160601.7486 | 160601.7486 | 160601.7486 | 160601.7486 | 160601.7486 | 160601.7486
OPEX |  | 72902.6821 | 72902.6821 | 72902.6821 | 72902.6821 | 72902.6821 | 72902.6821 | 72902.6821 | 72902.6821 | 72902.6821 | 72902.6821 | 72902.6821 | 72902.6821 | 72902.6821 | 72902.6821 | 72902.6821 | 72902.6821
Electricity cost |  | 291671.2382 | 297504.663 | 303454.7563 | 309523.8514 | 315714.3284 | 322028.615 | 328469.1873 | 335038.571 | 341739.3425 | 348574.1293 | 355545.6119 | 362656.5241 | 369909.6546 | 377307.8477 | 384854.0047 | 392551.0848
Energy Saved |  | -24840.3456 | -25337.1525 | -25843.8956 | -26360.7735 | -26887.9889 | -27425.7487 | -27974.2637 | -28533.749 | -29104.4239 | -29686.5124 | -30280.2427 | -30885.8475 | -31503.5645 | -32133.6358 | -32776.3085 | -33431.8347
Total Cost |  | -500335.3234 | -505671.9412 | -511115.2914 | -516667.5086 | -522330.7702 | -528107.297 | -533999.3543 | -540009.2528 | -546139.3492 | -552392.0476 | -558769.7999 | -565275.1073 | -571910.5208 | -578678.6427 | -585582.1269 | -592623.6808
Energy sold |  | 528016.65 | 538576.983 | 549348.5227 | 560335.4931 | 571542.203 | 582973.047 | 594632.508 | 606525.1581 | 618655.6613 | 631028.7745 | 643649.35 | 656522.337 | 669652.7838 | 683045.8394 | 696706.7562 | 710640.8913
P&L (yearly) |  | 27681.3266 | 32905.0418 | 38233.2312 | 43667.9845 | 49211.4328 | 54865.75 | 60633.1537 | 66515.9054 | 72516.3121 | 78636.7269 | 84879.5501 | 91247.2297 | 97742.2629 | 104367.1968 | 111124.6293 | 118017.2105
P&L (cumulative) |  | 27681.3266 | 60586.3684 | 98819.5997 | 142487.5841 | 191699.0169 | 246564.767 | 307197.9206 | 373713.826 | 446230.1381 | 524866.865 | 609746.4151 | 700993.6448 | 798735.9077 | 903103.1044 | 1014227.7338 | 1132244.9443
SCNEARIO 2 RESULTS : Calculation of the price of heat at the data center outlet
CAPEX | 599577.8146 | EUR
Subsidies | 0 | EUR
Total CAPEX | 599577.8146 | EUR
Annualised CAPEX (EUR/year) | 52273.9261 | EUR/year
Annual O&M - excluding electricity | 17987.3344 | EUR/year
Electricty Cost | 22629.3103 | EUR/year
Total Energy saved (EUR/year) | 25095.1516 | EUR/year
Contract duration | 20 | years
PUE (adjusted) | 1.3073 | -0.0013389 | PUE value after heat reuse, without electricity consumption by heat pumps operated by heat district operator
Total annual cost | 67795.4194 | EUR/year
Annual energy delivered | 5558.07 | MWh/year
DC Heat Price | 12.1977 | EUR/MWh

## PUE Impact
PUE Impacts - as defined by ISO 30134-2
PUE
Total EDC for last 12 months: (MWh) | 175200 | MWh
Total EIT for last 12 months: (MWh) | 133880 | MWH
PUE for last 12 months | 1.3086 | PUE value before heat reuse
SCENARIO 1-1 & 1-2
PUE for last 12 months | 1.3226 | PUE value after heat reuse, integrating electricity consumption by heat pumps operated by data center operator
SCENARIO 2
PUE for last 12 months | 1.3073 | PUE value after heat reuse, without electricity consumption by heat pumps operated by heat district operator

## Data (hidden)
Parameter | Value (enter) | Units | Comments
list menu
Project Name | PAR18 |  |  | Yes
Date | 2025-10-31 |  |  | No
TECHNICAL Data
Energy reused (MWh/anj) | 6000 | MWh
Energy recovered after losses and efficiencies (MWh) | 5558.07 | MWh
Usage rate (hours/year) | 3624 | h/an
Available power (kW) - maximum heat flow | 1655.6291 | kW
DC Outlet water temperature (°C) | 29 | °C
DC Inlet Water Temperature (°C) | 19 | °C
Desired outlet temperature (°C) | 85 | °C
Distance to the connexion point to the heating network (m) | 100 | m | one-way
Estimated average power consumption in free-cooling mode | 48 | kW | Dry cooler pumps substituted
Linear Casing Heat Loss (W/m.K) (est.) | 0.5 | W per m per K
Capture efficiency (fraction) | 0.95 | - | fraction
Heat exchanger efficiency (fraction) | 0.98 | - | fraction
Fractional network losses (%) | 5 | % | Heat losses on transport
Collector Target Speed (m/s) | 1.5 | m/s
Water density (kg/m3) | 1000
Cp water (kWh/kg.K) | 1.16
Local Specific Pressure Drop (kPa) - Additional | 5 | kPa
COP heat pump | 3.19 | NA | It is understood that COP will vary significantly with ambient and source temperature.
PUE
Total EDC for last 12 months: (MWh) | 175200 | MWh
Total EIT for last 12 months: (MWh) | 133880 | MWH
PUE for last 12 months | 1.3086
CAPEX (manually)
Exchanger cost (EUR) | 79470.1987 | EUR
PAC cost (EUR) | 1276490.0662 | EUR
Cost of pump & fixed equipment (EUR) | 248344.3709 | EUR
Electrical Connection Cost (EUR) | 149006.6225 | EUR
Control/Automation (EUR) | 184097.6821 | EUR
Study cost (EUR) | 87665.5629 | EUR
CAPEX (simulation)
Exchanger cost (EUR) | 79470.1987 | EUR | 48€/kW (equipment + installation)
PAC cost (EUR) | 1276490.0662 | EUR | 771 €/kW_th (equipment + installation)
Cost of pump & fixed equipment (EUR) | 248344.3709 | EUR | 150€/kW
Electrical Connection Cost (EUR) | 149006.6225 | EUR | 90 €/kW
Control/Automation (EUR) | 87665.5629 | EUR | 5% CAPEX
Study cost (EUR) | 184097.6821 | EUR | 10% CAPEX
Unknown Risk(EUR) | 405014.9007 | EUR | x% CAPEX
OPEX
Annual O&M (% of CAPEX) | 3 | %
Cost of electricity (EUR/kWh) | 0.14 | EUR/kWh
Subsidiary
Subsidiary (EUR) | 588000 | EUR
FINANCIAL Data
Amortization period (years) | 20 | ans
Discount rate (%) | 6 | %
Annuity Factor (CRF) | 0.087185
Heat price indexation | 2%
Electricity Inflation | 2%

## SeasonalFactor (hidden)
Month | Hours/ month | Seasonal Factor (0-1) | Simulated Operating Hour/ Month | Given Operating Hour/ Month | Adjusted Available Power (kW) | Energy Gross Month (MWh) | Energy recovered after losses and efficiencies (MWh)
Jan | 744 | 1 | 724.8 |  | 1655.6291 | 4348.8 | 4028.4891 | Broken circular ref; old formula: =$G$2
Feb | 672 | 1 | 724.8 |  | 1655.6291 | 4348.8 | 4028.4891
Mar | 744 | 1 | 724.8 |  | 1655.6291 | 4348.8 | 4028.4891
Apr | 720 | 0 | 0 |  | 0 | 0 | 0
May | 744 | 0 | 0 |  | 0 | 0 | 0
Jun | 720 | 0 | 0 |  | 0 | 0 | 0
Jul | 744 | 0 | 0 |  | 0 | 0 | 0
Aug | 744 | 0 | 0 |  | 0 | 0 | 0
Sep | 720 | 0 | 0 |  | 0 | 0 | 0
Oct | 744 | 0 | 0 |  | 0 | 0 | 0
Nov | 720 | 1 | 724.8 |  | 1655.6291 | 4348.8 | 4028.4891
Dec | 744 | 1 | 724.8 |  | 1655.6291 | 4348.8 | 4028.4891
Recoverable / potential energy (MWh/year) |  | 21744
Energy recovered / delivered (MWh/year) |  | 20142.4457

## Meteo data + EER (hidden)
Temperatures | hours | Chiller cooling capacity | Chiller EER | Chiller consumption | Chiller consumption
-5 | 1 | 1655.6291 | 113.92 | 14.5333 | 14.5333
-4 | 22 | 1655.6291 | 111.96 | 14.7877 | 325.3291
-3 | 36 | 1655.6291 | 110.07 | 15.0416 | 541.4977
-2 | 78 | 1655.6291 | 108.24 | 15.2959 | 1193.0809
-1 | 111 | 1655.6291 | 106.47 | 15.5502 | 1726.0715
0 | 152 | 1655.6291 | 104.76 | 15.804 | 2402.211
1 | 161 | 1655.6291 | 101.96 | 16.238 | 2614.3222
2 | 189 | 1655.6291 | 99.31 | 16.6713 | 3150.8801
3 | 260 | 1655.6291 | 96.8 | 17.1036 | 4446.9378
4 | 251 | 1655.6291 | 94.41 | 17.5366 | 4401.6832
5 | 301 | 1655.6291 | 92.13 | 17.9706 | 5409.1433
6 | 307 | 1655.6291 | 81.06 | 20.4247 | 6270.3941
7 | 349 | 1655.6291 | 72.36 | 22.8804 | 7985.276
8 | 309 | 1655.6291 | 65.34 | 25.3387 | 7829.6511
9 | 332 | 1655.6291 | 59.57 | 27.793 | 9227.2767
10 | 353 | 1655.6291 | 54.73 | 30.2509 | 10678.5508
11 | 293 | 1655.6291 | 30.16 | 54.8949 | 16084.1955
12 | 251 | 1655.6291 | 20.81 | 79.5593 | 19969.3856
13 | 207 | 1655.6291 | 15.89 | 104.1931 | 21567.9819
14 | 201 | 1655.6291 | 16.01 | 103.4122 | 20785.8499
15 | 141 | 1655.6291 | 15.78 | 104.9195 | 14793.6444
16 | 142 | 1655.6291 | 15.01 | 110.3017 | 15662.8473
17 | 109 | 1655.6291 | 13.92 | 118.9389 | 12964.3374
18 | 97 | 1655.6291 | 12.81 | 129.2451 | 12536.7702
19 | 83 | 1655.6291 | 11.5 | 143.9678 | 11949.3234
20 | 59 | 1655.6291 | 10.19 | 162.4759 | 9586.0765
21 | 37 | 1655.6291 | 10.48 | 157.9799 | 5845.2555
22 | 23 | 1655.6291 | 9.57 | 173.002 | 3979.046
23 | 17 | 1655.6291 | 8.59 | 192.7391 | 3276.5652
24 | 11 | 1655.6291 | 8.38 | 197.5691 | 2173.2602
25 | 8 | 1655.6291 | 7.67 | 215.8578 | 1726.8622
26 | 3 | 1655.6291 | 8.26 | 200.4394 | 601.3181
27 | 2 | 1655.6291 | 7.4 | 223.7337 | 447.4673
| 4896 |  |  | Energy Saved | 242167.0254
|  |  |  | Power Saved | 49.4622

## Calculations (hidden)
Calculating Topic | Values
DeltaT (K) | 10
Available rated power (kW) | 1655.6291
Mass flow rate m_dot (kg/s) | 39.6463
Volume flow rate Q (m3/s) | 0.039646
Estimated Collector Diameter (m) | 0.18345
Estimated Diameter (mm) | 183.447
Actual speed (m/s) | 1.5
Pressure Drop (Pa) | 1125
Approximate pump power (kW) | 44.6021
Approximate pump energy (kWh/year) | 161637.931
Power required to raise temperature (kW) | 2575.4231
Electrical power of the heat pump (kW) | 519.006
Energy consumed by the heat pump (kWh/year) | 1880877.7429
Data Center Power Saved (kW) | 49.4622
Energy saved by data center (kWh) | 179251.0825
Transmission heat losses (kW) | 1 | Note: At 1km the pipeline loss is no longer negligible, especially at 25–35°C supply temperature where the ΔT to ambient is small.
Transport loss fraction (%) | 0.0604
Heat Indexation | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Heat Price (€/kWh) | 95 | 96.9 | 98.838 | 100.8148 | 102.8311 | 104.8877 | 106.9854 | 109.1251 | 111.3076 | 113.5338 | 115.8045 | 118.1206 | 120.483 | 122.8926 | 125.3505 | 127.8575 | 130.4146 | 133.0229 | 135.6834 | 138.3971 | 141.165
Electricity Inflation | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Electricity Price (€/kWh) | 0.14 | 0.1428 | 0.14566 | 0.14857 | 0.15154 | 0.15457 | 0.15766 | 0.16082 | 0.16403 | 0.16731 | 0.17066 | 0.17407 | 0.17755 | 0.1811 | 0.18473 | 0.18842 | 0.19219 | 0.19603 | 0.19995 | 0.20395 | 0.20803

## Equipment References (hidden)
EQUIPMENT REFERENCE — HEAT PUMPS & HEAT EXCHANGERS FOR DC HEAT REUSE
European market reference data for ROM-stage cost estimation ¦ Prices are indicative benchmarks only — always obtain project-specific quotations from manufacturers ¦ Update the 'Local Price / Notes' column with your actual supplier quotes
HOW TO USE THIS TAB
1. Use this tab as a starting point when populating CAPEX assumptions in the 'Data' tab. The ROM ranges below reflect current European market intelligence (Q1 2026) but will change — update regularly. 2. Prices are equipment-supply only unless stated. Installed / turnkey costs are higher — see the 'Installed' column. 3. Column L (yellow) is your working column: enter the actual budgetary price received from your local supplier and the date. This overrides the ROM benchmark for your specific project.
SECTION 1 — HEAT PUMPS (water-source, waste heat recovery, district heating delivery)
Relevant range for DC heat reuse: 500 kW – 5 MW thermal output, lifting ~25–35°C source to 60–85°C delivery. The simulator (PAR18 example) requires ~1,655 kW thermal at 80–85°C — this sits in the mid-range of the platforms below.
Manufacturer | Product / Series | HQ Country | Capacity Range (thermal output) | Max Supply Temp (°C) | Refrigerant(s) | ROM Cost — Equipment Supply Only (€/kW th) | ROM Cost — Installed Turnkey (€/kW th) | Cost Basis (per unit or /kW) | Source / Last Verified | Local Price / Notes (update with your quote)
GEA Group | RedAstrum | Germany | 750 kW – 2,900 kW (standard range; custom beyond) | 55–80°C standard (higher on request) | Ammonia (R-717) screw compressor | €350 – 550 /kW th | €550 – 900 /kW th | Per kW thermal output | Market benchmark Q1 2026
GEA Group | RedGenium (next-gen) | Germany | Custom — higher temp / efficiency than RedAstrum | Up to 95°C+ | Ammonia (R-717) | €400 – 650 /kW th (premium vs RedAstrum) | €650 – 1,050 /kW th | Per kW thermal output | Market benchmark Q1 2026
Oilon | ChillHeat S (S600–S2000) | Finland | 600 kW – 5 MW per unit; cascadable | ~85°C max flow temp | HFC / HFO / Natural refrigerants | €300 – 500 /kW th | €500 – 850 /kW th | Per kW thermal output | Nordic project data + Pure Thermal UK Q1 2026
Oilon | ChillHeat RE series | Finland | 30 kW – 580 kW per unit | >60°C from cold inlet; up to ~70°C | HFC / HFO | €350 – 550 /kW th | €550 – 900 /kW th | Per kW thermal output | Oilon published range Q1 2026
Star Refrigeration (Azane platform) | Azane series | UK / Europe | 200 kW – 2 MW+ ammonia units | Up to 90°C | Ammonia (R-717) — low charge | €400 – 650 /kW th | €600 – 1,000 /kW th | Per kW thermal output | Star published data Q1 2026
MAN Energy Solutions (now Everllence) | HOFIM / ETES platform | Switzerland / DE | 10 MW – 90 MW+ per unit | 60–280°C | CO₂ (R-744) natural refrigerant | Not applicable at DC project scale (<5 MW) | Not applicable at DC project scale | MW-scale city DHN only | Helsinki / Esbjerg reference projects 2024 | ⚠ Only relevant for very large-scale DHN projects (10 MW+). Not suitable for typical DC heat reuse.
Siemens Energy | Industrial HP platform | Germany | 5 MW – 50 MW+ | Up to 160°C (high-temp variants) | Various | Not applicable at typical DC scale | Not applicable at typical DC scale | MW-scale DHN only | Market data Q1 2026 | ⚠ Relevant for large DHN utility investment. Not sized for <5 MW DC heat reuse projects.
Viessmann / Vitodens (commercial) | Vitocal 350-HT and custom industrial range | Germany | Up to ~2 MW (modular systems) | 75°C standard; 85°C high-temp variants | R-134a / R-1234ze HFO low-GWP | €350 – 600 /kW th | €550 – 950 /kW th | Per kW thermal output | Viessmann commercial data Q1 2026
Friotherm (Sulzer Group) | Unitop series (Unitop 50FY and variants) | Switzerland | 1 MW – 30 MW per unit | Up to 90°C (standard) | R-134a / R-1234ze | €400 – 700 /kW th | €650 – 1,100 /kW th | Per kW thermal output | Project references Europe Q1 2026
SECTION 2 — HEAT EXCHANGERS (primary interface: DC cooling loop → heat pump evaporator)
A primary plate heat exchanger (PHE) is installed at the DC cooling loop interface to provide hydraulic separation and prevent contamination. At 1–2 MW thermal, this is a relatively modest unit (100–500 plates). The simulator uses €50/kW (€83k for 1,655 kW) — this is reasonable if equipment-only and single-duty.
Manufacturer | Product / Series | HQ Country | Capacity Range (thermal duty) | Max Operating Temp / Pressure | Construction Type | ROM Cost — Equipment (€/kW th or indicative unit) | Installed Cost (equipment + installation) | Cost Basis | Source / Last Verified | Local Price / Notes (update with your quote)
Alfa Laval | M-series Gasketed Plate & Frame (M15, M20, M30) | Sweden | 100 kW – 10 MW+ (add plates to scale) | Up to 180°C / 25 bar (standard grades) | Gasketed plate & frame (GPHE) stainless steel or titanium | €15 – 45/kW th (equipment only) ~€15k–75k typical for 1–2 MW unit | €25 – 70/kW th (inc. frame, connections and basic installation) | Per kW thermal duty at design conditions | Alfa Laval published range Q1 2026
Alfa Laval | T-series Gasketed (T20, T35 etc.) general industrial | Sweden | 50 kW – 5 MW+ | Up to 150°C / 16 bar | Gasketed plate & frame | €12 – 40/kW th (slightly lower than M-series) | €20 – 60/kW th | Per kW thermal duty | Alfa Laval market data Q1 2026
Kelvion | NT / NTL series Gasketed PHE | Germany | 100 kW – 10 MW+ | Up to 180°C / 25 bar | Gasketed plate & frame stainless / titanium | €13 – 42/kW th (competitive with Alfa Laval) | €22 – 65/kW th | Per kW thermal duty | Kelvion market data Q1 2026
SWEP (Dover Corp.) | B-series Brazed Plate (B250, B400 etc.) | Sweden | 50 kW – 1 MW (larger duties use multiple units) | Up to 225°C / 45 bar | Brazed stainless steel - compact, no gaskets | €20 – 60/kW th (higher per kW due to compact format) | €30 – 80/kW th | Per kW thermal duty | SWEP / market Q1 2026 | Typically used inside HP unit (evaporator / condenser). Less common as primary DC interface exchanger above 500 kW.
Danfoss | XB / XGC series Brazed & Gasketed PHE | Denmark | 20 kW – 2 MW+ | Up to 180°C / 30 bar | Brazed or gasketed PHE | €18 – 55/kW th | €28 – 75/kW th | Per kW thermal duty | Danfoss market data Q1 2026
Tranter (part of Alfa Laval Group) | GC / GX Gasketed PHE — industrial grade | USA / Europe | 200 kW – 20 MW+ | Up to 200°C / 25 bar | Gasketed plate & frame - heavy industrial | €20 – 50/kW th | €30 – 75/kW th | Per kW thermal duty | Market benchmark Q1 2026
SECTION 3 — CAPEX RATE BENCHMARK vs SIMULATOR ASSUMPTIONS (for 1,655 kW thermal — PAR18 example)
Cost Item | Simulator Rate (simulated mode) | Simulator Total (€) | Market ROM Low (€/kW) | Market ROM High (€/kW) | Market Total Low (€) | Market Total High (€) | Gap Assessment |  |  | Comments
Heat Pump (PAC) | €300/kW th | 496689 | 350 | 600 | 579250 | 993000 | ⚠ UNDERSTATED |  |  | Simulator uses equipment-supply rate only. Market range is wider and installation adds 30–50% on top. Recommend €400–600/kW as ROM minimum.
Primary Heat Exchanger | €50/kW th | 82781 | 15 | 50 | 24825 | 82750 | ✓ REASONABLE |  |  | At upper end of market range - acceptable if it includes frame, connections and installation. Cross-check with Alfa Laval / Kelvion budgetary quote.
Pumps & Fixed Equipment | €150/kW th | 248344 | 100 | 200 | 165500 | 331000 | ✓ REASONABLE |  |  | Reasonable for circulation pumps, pipework, valves and ancillary equipment within the plant room.
Electrical Connection | €70/kW th | 115894 | 70 | €300+ | 115894 | €496,500+ | ⚠ POTENTIALLY UNDERSTATED |  |  | If this covers only in-house cabling, €70/kW is plausible. If it is meant to include DSO grid reinforcement for the HP load, it is severely understated - grid connection alone can be €200–500k irrespective of capacity.
Control / Automation | €60/kW th (10% CAPEX note in Data) | 99089 | 30 | 80 | 49650 | 132400 | ✓ REASONABLE |  |  | Reasonable for SCADA, instrumentation, metering and interface with DC BMS. Confirm scope includes DHN metering interface.
Study / Engineering | €5% CAPEX | 47185 | 5–10% | 10–15% | 59950 | 149850 | ⚠ LOW FOR ROM STAGE |  |  | 5% is appropriate for detailed design. For ROM/feasibility stage the study cost to reach FID is typically 8–15% of total CAPEX. Consider increasing.
Contingency | 10% CAPEX | 108998 | 15% | 25% | 149850 | 249750 | ⚠ LOW FOR ROM STAGE |  |  | 10% contingency is appropriate for detailed design. ROM-stage contingency should be 20–30% to reflect uncertainty in scope and pricing.
Civil Works / Pipeline (ABSENT from simulator) | — NOT INCLUDED — | 0 | €150/m (greenfield) | €2,500/m (urban) | €15,000 (100m greenfield) | €250,000+ (100m urban) | ⚠ MISSING COST LINE |  |  | Critical gap. Even at 100m (the PAR18 example), civil works for pipeline installation could add €15k–250k depending on urban/greenfield. Must be added as a parametric input.
IMPORTANT: All prices are indicative ROM benchmarks for early-stage feasibility only. Actual prices depend on project-specific scope, site conditions, refrigerant choice, delivery programme, country of installation and prevailing market conditions. Always obtain written budgetary quotations from at least two manufacturers before using these figures in any investment decision. Prices correct to Q1 2026 — update the 'Last Verified' column when refreshing data.